## Pricing
ECMWF/RFP/2025/397 ANNEX 2 PRICING TABLES
| CODE | DESCRIPTION OF WORKS | UNIT | QUANTITY
MECHANICAL WORKS
1 | NP.001 | Supply and installation of chiller with screw compressor type Mitsubishi i-FR-G05 3602. Outdoor unit for chilled water production with variable-speed semi-hermetic screw compressors suitable for R513A, axial fans, microchannel aluminum condenser coils, single-pass shell-and-tube evaporator, and electronic expansion valve. Steel sheet base, frame and panels painted with polyester powder. Eurovent certified. Compressors with integrated inverter, refrigerant-cooled, with automatic compression ratio adjustment based on operating conditions. NOMINAL CAPACITY: 865 kW; TOTAL POWER INPUT: 249 kW; 400/3/50[V/pH/Hz]; Dimensions: 2260x9000xh2500 mm; Ambient Temp: 39.5°C; Supply Temp: 15°C; Return Temp: 21°C; Weight: 8500 kg. Machine configuration as per technical specifications. Including factory-attended testing. Delivered and installed in accordance with best practices and fully operational. | each | 1
2 | M.02.01.01.12 | Supply and installation of seamless black steel pipe UNI 10255 Ø 6", for external CT lines. Medium series, EN 10255 compliant, with conformity certificate. Includes fittings, deburring, surface cleaning, oxyacetylene welding, proper slope installation, brackets and anchors, anti-rust coating. CAM-compliant. Black steel pipe Victaulic Markup for Victaulic joints (15%) | m m | 54 8
3 | M.03.02.01.03 | Supply and installation of synthetic rubber insulation (sheet or sleeve), for hot, cold, and chilled water pipes, including bends and fittings. Thermal conductivity compliant with DPR 412/93, fire reaction class per DM 15-03-2005. Thickness: 60 mm. Conductivity: 0.04 W/m·K. | m2 | 29,50
4 | M.03.04.02.01 | Supply and installation of aluminum cladding shells, thickness 6/10 mm, fixed with self-tapping screws resistant to atmospheric agents. Special pieces (elbows, tees) made in segments. For inspectable equipment, install hinged aluminum box with lever closure. For piping. | m2 | 29,50
5 | N04.013.020.c | Mobile crane 30,000 kg for lifting DN150 pipe sections. | h | 2
6 | M.05.04.10 | Supply and installation of anti-vibration joints, rubber body, cylindrical vulcanized rubber, suitable up to 110°C. For DN150, with flanges per UNI-DIN PN10, bolts DIN931, washers DIN125. | each | 4
7 | M.03.06.02 | Supply and installation of insulation for valves of any diameter. | each | 5
8 | M.25.03 | Static pipe support system with floor-mounted frame and slotted profiles, minimum 45 mm brackets. Includes galvanized steel frame and profiles, quick-connect accessories, EPDM/SBR rubber-lined clamps, bolts, anchors, and structural compliance report signed by qualified technician. | each | 14
9 | M.25.04 | Static pipe support system with seismic configuration for heat pump, including stabilizing tie rods, compliance report signed by qualified technician. Brackets for flat pipe support with structural calculation report Seismic heat pump support to be constructed as per the instructions given in the CSA - accompanied by a calculation report | each each | 4 6
10 | M.03.04.02.04 | Aluminum cladding shells for valves, same specs as piping cladding. | each | 5
11 | M.11.05.02.03 | Supply and installation of expansion vessel with non-toxic membrane for water-sanitary systems compliant with DM 21/3/73. Capacity 12 liters | each | 1
12 | M.11.01.05.02 | Supply and installation of dial pressure gauge with radial connection. Dial size DN 80 | each | 2
13 | LOM251.OC.EEA.Pa01.F9740.Za001.0750 | Supply and installation of OP Thermometer with radial stem; function: temperature measurement; application: piping; dial size [mm] = 80. Included: thermowell | each | 2
14 | M.11.03.01.03 | Supply and installation of diaphragm-type safety valve approved by INAIL, standard settings up to 6.0 bar. DN 25 (1 x 1 1/4") Safety valve sets at 4 bars | each | 1
15 | M.04.01.20.05 | Supply and installation of butterfly valve, manual operation, type ... 6, complete with counter flanges, bolts and gaskets DN 150 | each | 2
16 | M.12.03.16 | Supply and installation of immersion temperature probe with plastic housing, brass sheath, PT1000 sensor at 0°C, temperature range -30/+130°C, immersion length up to 300 mm | each | 2
17 | M01.001.025 | Worker category 5 Dismantling of 2 lightning protection poles Restoration of 2 lightning protection poles at end of works | h h | 2 2
18 | M01.001.035 | Worker category 3 Dismantling of 2 lightning protection poles Restoration of 2 lightning protection poles at end of works | h h | 4 4
19 | M01.001.025 | Worker category 5 Plumbing labor for the following modifications: relocation of existing valve, modification of T-fitting (90° rotation) | h h | 4 6
20 | M01.001.035 | Worker category 3 Plumbing labor for the following modifications: relocation of existing valve, modification of T-fitting (90° rotation) | h h | 4 4 | Total price (EUR)
Mechanical components costs including work costs
ELECTRICAL SYSTEM
21 | D02.001.055.k | Supply and installation of flexible cable FG16M16 0.6/1 kV, 240 mm² section, CEI 20-13 compliant, low smoke and halogen-free, fire retardant. Connection between ME-SW-2 and chiller, Connection between ME-SW-4 and chiller. | m m | 600 600
22 | E.01.01.03.0.15 | Supply and installation of unshielded flexible cable FG17 450/750V, 240 mm² section, CPR compliant. Connection between main grounding collector and chiller. | m m | 30
23 | E.01.02.04.0.48 | Supply and installation of fixed cable FG16M16 / FG16OM16 0.6/1 kV, 7x1.5 mm² section, CPR compliant. Connection between ClimaPro Master and chiller. | m m | 80
24 | E.01.02.08.0.01 | Supply and installation of shielded fixed cable FG16OH2M16 0.6/1 kV, 2x1.5 mm² section, CPR compliant. Multiple connections between ClimaPro Master and sensors, flow meter, ClimaPro Slave, and Schneider panel. Link ClimaPro Master and temperature sensor Link ClimaPro Master and temperature sensor Link ClimaPro Master and flow meter Link ClimaPro Master and ClimaPro Slave Link ClimaPro Master and ClimaPro Slave Link 3 DI and 1 DO between Schneider panel and chiller | m m | 80 80 80 10 10 10 480
25 | E.01.02.04.0.50 | Supply and installation of fixed cable FG16M16 / FG16OM16 0.6/1 kV, 10x1.5 mm² section, CPR compliant. Connection between ClimaPro Master and SUB-SW-B1. | m | 80
26 | E.01.02.04.0.48 | Supply and installation of fixed cable FG16M16 / FG16OM16 0.6/1 kV, 7x1.5 mm² section, CPR compliant. Connection between ClimaPro Master and ClimaPro Slave. | m | 10
27 | D02.001.065.a | Supply and installation of flexible cable FG16OM16 0.6/1 kV, 3x1.5 mm² section, CPR compliant. Link between ClimaPro Master and the flow meter Link between ClimaPro Master and ClimaPro Slave. | m m | 80 10 | Total price (EUR)
Electrical systems cost including work costs
PROGRAMMING
28 | NP.003 | Supply and commissioning of programming activities for integration of chiller “CH2N” into BMS system at ECMWF Bologna. Includes: IP list update, Modbus and BACnet interfaces (14 variables), software and alarm creation, electrical diagram updates, hardwired points (3 DI, 1 DO), commissioning, and graphical interface setup on Enterprise Server. Delivered and installed to best practice and fully operational. | Lumpsum | 1
29 | NP.002 | Modification of ClimaPRO electrical diagrams for integration into supervision system: chiller CH2N, 2 temperature sensors, flow meter. Includes logic update, system setup, and commissioning of sensors and transducers. | Lumpsum | 1
30 | NP.004 | Supply and installation of modification to QE SUB SW B1 panel: insertion of IP-IO-UIO5DOFA4 board, accessories, power supply, electrical diagram revision, and subcontracted site work. Delivered and installed to best practice and fully operational. | Lumpsum | 1 | Total price (EUR)
Programming cost
Total price (EUR)
TOTAL COST
V B